## Sheet1 (hidden)
01301100 | 10301100 | 0 | 0001 | 0011 | 0000 | 0001 | 0001 | 0000 | 0000
01301D00 | 10301D00 | 0 | 0001 | 0011 | 0000 | 0001 | 1101 | 0000 | 0000
01901100 | 10901100 | 0 | 0001 | 1001 | 0000 | 0001 | 0001 | 0000 | 0000
|  |  |  | 0101 | 0000
01901200 | 10901200 | 0 | 0001 | 1001 | 0000 | 0001 | 0010 | 0000 | 0000
|  |  |  | 0101 | 0000
0D202100 | 1C202100 | 0 | 1101 | 0010 | 0000 | 0010 | 0001 | 0000 | 0000
0D202F00 | 1C202F00 | 0 | 1101 | 0010 | 0000 | 0010 | 1111 | 0000 | 0000
0D203100 | 1C203100 | 0 | 1101 | 0010 | 0000 | 0011 | 0001 | 0000 | 0000
11204100 | 10204100 | 1 | 0001 | 0010 | 0000 | 0100 | 0001 | 0000 | 0000
11204F00 | 10204F00 | 1 | 0001 | 0010 | 0000 | 0100 | 1111 | 0000 | 0000
| 5 |  |  |  | 0000 | 0101
15208100 | 14208100 | 1 | 0101 | 0010 | 0000 | 1000 | 0001 | 0000 | 0000
| 9 |  |  |  | 0000 | 1001
15208F00 | 14208F00 | 1 | 0101 | 0010 | 0000 | 1000 | 1111 | 0000 | 0000
0001
0011
0CF20101 | 1CF20101 | 0 | 1100 | 1111 | 0010 | 0000 | 0001 | 0000 | 0001
0CF20201 | 1CF20201 | 0 | 1100 | 1111 | 0010 | 0000 | 0010 | 0000 | 0001
待屏蔽 | B |  |  | 0111
080a0aff | 180a0aff | 0 | 1000 | 0000 | 1010 | 0000 | 1010 | 1111 | 1111
080a0bff | 180a0bff | 0 | 1000 | 0000 | 1010 | 0000 | 1011 | 1111 | 1111
080a05ff | 180a05ff | 0 | 1000 | 0000 | 1010 | 0000 | 0101 | 1111 | 1111
0CF20301 | 1CF20301 | 0 | 1100 | 1111 | 0010 | 0000 | 0011 | 0000 | 0001
0CF20401 | 1CF20401 | 0 | 1100 | 1111 | 0010 | 0000 | 0100 | 0000 | 0001
08f50A01 | 18f50A01 | 0 | 1000 | 1111 | 0101 | 0000 | 1010 | 0000 | 0001
04F10B00 | 14F10B00 | 0 | 0100 | 1111 | 0001 | 0000 | 1011 | 0000 | 0000
0CF20801 | 1CF20801 | 0 | 1100 | 1111 | 0010 | 0000 | 1000 | 0000 | 0001
08f50B01 | 18f50B01 | 0 | 1000 | 1111 | 0101 | 0000 | 1011 | 0000 | 0001
04F10C00 | 14F10C00 | 0 | 0100 | 1111 | 0001 | 0000 | 1100 | 0000 | 0000
0CF20901 | 1CF20901 | 0 | 1100 | 1111 | 0010 | 0000 | 1001 | 0000 | 0001
| D | 9 | F | F | 1101 | F | F | F | F | 0x9FFDFFFF
|  | 9 | F | F | D | 3 | F | F | F | 0x9FFD3FFF
|  | 9 | F | F | D | 0 | F | F | F | 0x9FFD1FFF
|  | 9 | F | F | F | 9 | F | 0 | F | 0x9FDF9FFF
|  | 9 | F | F | F | F | 3 | F | F | 0x9FFFF3FF
| 00301100 | 0000 | 0001 | 0001 | 1010
| 00301D00 | 0000 | 0001 | 1101
| 00901100 | 0000 | 0001 | 0001 | [8 empty] | 00301100 |  | 00301100
| 00901200 | 0000 | 0001 | 0010 | [8 empty] | 00301D00 |  | 00301D00
| 0C202100 | 0000 | 0010 | 0001 | [8 empty] | 00901100 | 00901100 | 00901100
| 0C202F00 | 0000 | 0010 | 1111
| 0C203100 | 0000 | 0011 | 0001 | [8 empty] | 00901200 | 00901200 | 00901200
| 10204100 | 0000 | 0100 | 0001 | [7 empty] | 00301100
| 10204F00 | 0000 | 0100 | 1111 | [7 empty] | 00301D00 | 0C202100 |  | 0C202100
| 14208100 | 0000 | 1000 | 0001 | [7 empty] | 00901100 | 0C202F00 |  | 0C202F00
| 14208F00 | 0000 | 1000 | 1111 | [7 empty] | 00901200 | 0C203100 |  | 0C203100
| ##DFF## | [9 empty] | 0x9FFD0FFF | 0x9FFD1FFF | 0x9FFD3FFF | 0x9FDF9FFF
| 08f50A01 | 0101 | 0000 | 1010 | [6 empty] | 08f50A01 | 08f50A01 | 08f50A01 | 080a0aff | 08f50A01
| 04F10B00 | 0001 | 0000 | 1011 | [6 empty] | 04F10B00 | 04F10B00 | 04F10B00 | 080a0bff | 04F10B00
| 08f50B01 | 0101 | 0000 | 1011 | [6 empty] | 08f50B01 | 08f50B01 | 08f50B01 | 080a05ff | 08f50B01
| 04F10C00 | 0001 | 0000 | 1100 | [6 empty] | 04F10C00 | 04F10C00 | 04F10C00 |  | 04F10C00
| ##9FF## | 1001
| ##2FF## | 10
| ##AFF## | 1010
0x9FFFF3FF

## Inverter modbusRTU (ID == 4)
Register Address（decimalism） | Register Type | Register Name | Physical Unit | Effective Range | note
Inverter Control Message
20000 | RO | The type of machine High | PH/EP/PV
20001 | RO | The type of machine Low | 1800/3000
20002 | RW | Serial number High
20003 | RW | Serial number Low
20004 | RO | Hardware version | 1.00.00
20005 | RO | Software version | 1.00.00
20006 | RO | Communication Protocal Edition | 1.00.00 |  | 1.04.15
20007-20008 | RW | reserved | reserved
20009 | RW | Battery voltage calibration coefficient | 16384 |  | X=(actual value/displayed value)*last calibration value, or 0xffff (-1) as no correction. For base value use 16384
20010 | RW | Inverter voltage calibration coefficient | 16384
20011 | RW | Grid voltage calibration coefficient | 16384
20012 | RW | Bus voltage calibration coefficient | 16384
20013 | RW | Control Current calibration coefficient | 16384
20014 | RW | Inverter Current calibration coefficient | 16384
20015 | RW | Grid Current calibration coefficient | 16384
20016 | RW | Load Current calibration coefficient | 16384
20101 | RW | Inverter offgrid work enable | 0：OFF 1：ON | effective range：0,1 the default value is 1； | 1:Turn on the inverter output when the grid is off. 0:Shut down the inverter output when the grid is off.
20102 | RW | Inverter output voltage Set | 220.0V-240.0V | (2200-2400) | Set the output voltage amplitude.
20103 | RW | Inverter output frequency Set | 50.00Hz/60.00Hz | 5000/6000 | Set the output frequency.
20104 | RW | Inverter search mode enable | 0：OFF 1：ON | effective range：0,1 the default value is 0； | 0:If disabled, no matter connect load is low or high, the on/off status of inverter output will not be effected. 1:If enable, the inverter begins search mode if the AC load connected is pretty low or not detected. The inverter’s “search” mode reduces stand-by energy consumption during no-load conditions.
20105 | RW | ONGrid switch | 0:OFF,1: ON | effective range：0,1 the default value is 0； | 0: Inverter detached from grid, using only PV and battery, 1: Inverter connected to the grid
20108 | RW | Inverter discharger to grid enable | 48V: 0：OFF 1：ON 24V: Null | effective range：0,1 the default value is 1； | 1:Enable Inveter discharging from battery to grid when the Inverter is connnectted to Grid 0:Disable Inveter discharging from battery to grid when the Inverter is connnectted to Grid
20109 | RW | Energy use mode | 48V:1:SBU;2:SUB;3:UTI;4:SOL (for PV;PH) 1:BAU; 3:UTI;4:BOU (for EP) 12V 24V:1:SBU;;3:UTI;4:SOL (for PV;PH) 1:BU; 3:UTI (for EP) |  | refer to user's manual
20111 | RW | Grid protect standard | 0：VDE4105; 1：UPS ; 2：home ;3:GEN |  | refer to user's manual
20112 | RW | SolarUse Aim | 0:LBU 1:BLU(defalut)(for PV;PH) 0:LB 1:LU(defalut) (for EP)
20113 | RW | Inverter max discharger current | 48V: 0.1A（AC） 12V 24V: Null | 1.0A-21.7A（10-217） | Set the max discharging current from Inverter
20118 | RW | Battery stop discharging voltage | 0.1V | 440~580(44.0-58.0)V the default value is 46.0V | refer to user's manual
20119 | RW | Battery stop charging voltage | 0.1V | 440~580(44.0-58.0)V the default value is 54.0V | refer to user's manual
20125 | RW | Grid max charger current set | 0.1A(DC) | 10~800(1.0-80.0)A the default value is 60.0A
20127 | RW | Battery low voltage | 0.1V | 400~480(40.0-48.0)V the default value is 40.8V
20128 | RW | Battery high voltage | 0.1V | 580~600(58.0-60.0)V the default value is 60.0V
20132 | RW | Max Combine charger current | 0.1A(DC)(for PV;PH) | 10~1400(1.0-140.0)A the default value is 60.0A
20142 | RW | System setting |  | refer to the frame System setting bit
20143 | RW | Charger source priority | 0:Soalr first (for PV;PH) 2:Solar and Utility(default) (for PV;PH) 3:Only Solar (for PV;PH) 2:Utility charger enable (default) (for EP) 3:Utility charger disable (for EP)
20144 | RW | Solar power balance | 0:SBD 1:SBE
20213 | RW | Remove the accumulated data | 0：No remove the accumulated data 1：Remove the accumulated data | the default value is 0; effective range:0,1
20214 | RW | Reset the parameter | 0：No effect 1：Action | the default value is 0; effective range:0,1
Register Address（decimalism） | Register Type | Register Name | Physical Unit | Effective Range | note
Inverter Display Message
25201 | RO | work state | 0:PowerOn 1:SelfTest 2:OffGrid 3:Grid-Tie 4:ByPass 5:Stop 6:Grid charging
25202 | RO | AC voltage grade | 230:230V 120:120V
25203 | RO | Rated power(VA) | VA
25204 | RO | reserved
25205 | RO | Battery voltage | 0.1V
25206 | RO | Inverter voltage | 0.1V
25207 | RO | Grid voltage | 0.1V
25208 | RO | BUS voltage | 0.1V
25209 | RO | Control current | 0.1A
25210 | RO | Inverter current | 0.1A
25211 | RO | Grid current | 0.1A
25212 | RO | Load current | 0.1A
25213 | RO | PInverter | 1W
25214 | RO | PGrid | 1W
25215 | RO | PLoad | 1W
25216 | RO | Load percent | 1% | new
25217 | RO | SInverter | 1VA
25218 | RO | SGrid | 1VA
25219 | RO | Sload | 1VA
25220 | RO | reserved
25221 | RO | Qinverter | 1var
25222 | RO | Qgrid | 1var
25223 | RO | Qload | 1var
25224 | RO | reserved
25225 | RO | Inverter frequency | 0.01Hz
25226 | RO | Grid frequency | 0.01Hz
25227 | RO | reserved
25228 | RO | reserved
25229 | RO | Inverter max number
25230 | RO | Combine type
25231 | RO | Inverter number
25232 | RO | reserved
25233 | RO | AC radiator temperature | 1℃
25234 | RO | Transformer temperature | 1℃
25235 | RO | DC radiator temperature | 1℃
25236 | RO | reserved
25237 | RO | Inverter relay state | 0: Disconnect 1:Connect
25238 | RO | Grid relay state | 0: Disconnect 1:Connect
25239 | RO | Load relay state | 0: Disconnect 1:Connect
25240 | RO | N_Line relay state | 0: Disconnect 1:Connect
25241 | RO | DC relay state | 0: Disconnect 1:Connect
25242 | RO | Earth relay state | 0: Disconnect 1:Connect
25243 | RO | reserved
25244 | RO | reserved
25245 | RO | Accumulated charger power high | 1000KWH
25246 | RO | Accumulated charger power low | 0.1KWH
25247 | RO | Accumulated discharger power high | 1000KWH
25248 | RO | Accumulated discharger power low | 0.1KWH
25249 | RO | Accumulated buy power high | 1000KWH
25250 | RO | Accumulated buy power low | 0.1KWH
25251 | RO | Accumulated sell power high | 1000KWH
25252 | RO | Accumulated sell power low | 0.1KWH
25253 | RO | Accumulated load power high | 1000KWH
25254 | RO | Accumulated load power low | 0.1KWH
25255 | RO | Accumulated self_use power high | 1000KWH
25256 | RO | Accumulated self_use power low | 0.1KWH
25257 | RO | Accumulated PV_sell power high | 1000KWH
25258 | RO | Accumulated PV_sell power low | 0.1KWH
25259 | RO | Accumulated grid_charger power high | 1000KWH
25260 | RO | Accumulated grid_charger power low | 0.1KWH
25261 | RO | Error message 1 |  | Refer to frame Error message 1
25262 | RO | Error message 2 |  | Refer to frame Error message 2
25263 | RO | Error message 3 |  | Refer to frame Error message 3
25264 | RO | reserved
25265 | RO | Warning message 1 |  | Refer to frame Warning message 1
25266 | RO | Warning message 2 |  | Refer to frame Warning message 2
25267 | RO | reserved
25268 | RO | reserved
25269 | RO | Serial number High
25270 | RO | Serial number Low
25271 | RO | Hardware version | 1.00.00
25272 | RO | Software version | 1.00.00
25273 | RO | Batt power | W
25274 | RO | Batt current | A
25275 | RO | Batt voltage grade | 48:48V 24:24V 12:12V
25276 |  | reserved
25277 | RO | Rated power(W) | W
25278 | RO | Communication Protocal Edition | 1.00.00 |  | 1.04.15
25279 | RO | Arrow Flag | bit |  | Refer to the frame Arrow Flag bit
System setting bit
Bit | meaning
0 | OverLoadRestartForbid
1 | OverTempRestartForbid
2 | OverLoadBypassForbid
3 | AutoTurnPageFlagForbid
4 | GridBuzzEnable(only use by PV1800)
5 | BuzzForbide(only use by PV1800)
6 | LcdLightEnable
7 | RecordFaultForbid
8 | reserved
9 | reserved
10 | reserved
11 | reserved
12 | reserved
13 | reserved
14 | reserved
15 | reserved
Arrow Flag bit
Bit |  | meaning
0 | PVFlag | 0:Inexistence 1:Existence
1 | LoadFlag | 0:Inexistence 1:Existence
2 | BattFlag | 0:Inexistence 1:Existence
3 | GridFlag | 0:Inexistence 1:Existence
4 | PV-to-Machine-Arrow | 0:Disconnect 1:PV-to-Machine
5 | Machine-to-Load-Arrow | 0:Disconnect 1:Machine-to-Load
6 | Machine-Batt-Arrow | 00:Disconnect 01:Machine-to-Batt 10:Batt-to-Machine 11:Connect
7
8 | Machine-Grid-Arrow | 00:Disconnect 01:Machine-to-Grid 10:Grid-to-Machine 11:Connect
9
10 | reserved
11 | reserved
12 | reserved
13 | reserved
14 | reserved
15 | reserved

## Inverter Alarm
Inverter error message 1 |  |  | Inverter warning message 1
Bit | meaning | description | Inverter Warning message 1 | meaning | description
0 | Fan is locked when inverter is off | 0：normal 1：fault | 0 | Fan is locked when inverter is on. | 0：normal 1：fault
1 | Inverter transformer over temperature | 0：normal 1：fault | 1 | Fan2 is locked when inverter is on. | 0：normal 1：fault
2 | battery voltage is too high | 0：normal 1：fault | 2 | Battery is over-charged. | 0：normal 1：fault
3 | battery voltage is too low | 0：normal 1：fault | 3 | Low battery | 0：normal 1：fault
4 | Output short circuited | 0：normal 1：fault | 4 | Overload | 0：normal 1：fault
5 | Inverter output voltage is high | 0：normal 1：fault | 5 | Output power derating | 0：normal 1：fault
6 | Overload time out | 0：normal 1：fault | 6 | Solar charger stops due to low battery. | 0：normal 1：fault
7 | Inverter bus voltage is too high | 0：normal 1：fault | 7 | Solar charger stops due to high PV voltage. | 0：normal 1：fault
8 | Bus soft start failed | 0：normal 1：fault | 8 | Solar charger stops due to over load. | 0：normal 1：fault
9 | Main relay failed | 0：normal 1：fault | 9 | Solar charger over temperature | 0：normal 1：fault
10 | Inverter output voltage sensor error | 0：normal 1：fault | 10 | PV charger communication error | 0：normal 1：fault
11 | Inverter grid voltage sensor error | 0：normal 1：fault | 11 | reserved | 0：normal 1：fault
12 | Inverter output current sensor error | 0：normal 1：fault | 12 | reserved | 0：normal 1：fault
13 | Inverter grid current sensor error | 0：normal 1：fault | 13 | reserved | 0：normal 1：fault
14 | Inverter load current sensor error | 0：normal 1：fault | 14 | reserved | 0：normal 1：fault
15 | Inverter grid over current error | 0：normal 1：fault | 15 | reserved | 0：normal 1：fault
Inverter error message 2 |  |  | Inverter warning message 2
Bit | meaning | description | Inverter Warning message 2 | meaning | description
0 | Inverter radiator over temperature | 0：normal 1：fault | 0 | reserved | 0：normal 1：fault
1 | Solar charger battery voltage class error | 0：normal 1：fault | 1 | reserved | 0：normal 1：fault
2 | Solar charger current sensor error | 0：normal 1：fault | 2 | reserved | 0：normal 1：fault
3 | Solar charger current is uncontrollable | 0：normal 1：fault | 3 | reserved | 0：normal 1：fault
4 | Inverter grid voltage is low | 0：normal 1：fault | 4 | reserved | 0：normal 1：fault
5 | Inverter grid voltage is high | 0：normal 1：fault | 5 | reserved | 0：normal 1：fault
6 | Inverter grid under frequency | 0：normal 1：fault | 6 | reserved | 0：normal 1：fault
7 | Inverter grid over frequency | 0：normal 1：fault | 7 | reserved | 0：normal 1：fault
8 | Inverter over current protection error | 0：normal 1：fault | 8 | reserved | 0：normal 1：fault
9 | Inverter bus voltage is too low | 0：normal 1：fault | 9 | reserved | 0：normal 1：fault
10 | Inverter soft start failed | 0：normal 1：fault | 10 | reserved | 0：normal 1：fault
11 | Over DC voltage in AC output | 0：normal 1：fault | 11 | reserved | 0：normal 1：fault
12 | Battery connection is open | 0：normal 1：fault | 12 | reserved | 0：normal 1：fault
13 | Inverter control current sensor error | 0：normal 1：fault | 13 | reserved | 0：normal 1：fault
14 | Inverter output voltage is too low | 0：normal 1：fault | 14 | reserved | 0：normal 1：fault
15 | reserved | 0：normal 1：fault | 15 | reserved | 0：normal 1：fault

## PV Charger ModbusRtu (ID == 4)
Register Address（decimalism） | Register Type | Register Name |  | Effective Range | note
PV Charger Control Message
10001 | RO | The type of machine | PC1600
10002 | WR | Serial number High
10003 | WR | Serial number Low
10004 | RO | Hardware version | 1.0.00
10005 | RO | Software version | 1.0.00
10006 | WR | PV voltage calibration coefficient | 16384
10007 | WR | Battery voltage calibration coefficient | 16384
10008 | WR | Charger current calibration coefficient | 16384
10009-10100 | WR | reserved | reserved
10103 | WR | Float voltage | 0.1V | 480~584(48.0-58.4)V the default value is 54.0V
10104 | WR | Absorption voltage | 0.1V | 480~584(48.0-58.4)V the default value is 56.4V
10105 | WR | Battery low voltage(for PV;PH) | 0.1V | 340~440(34.0-44.0)V the default value is 34.0V
10106 | WR | reserved
10107 | WR | Battery High voltage(for PV;PH) | 0.1V | 580~600(58.0-60.0)V the default value is 60.0V
10108 | WR | PV max charger current(for PV;PH) | 0.1A | 0.1A effective range：(0-80.0)A
10110 | WR | Battery type | 0:no choose 1:Use defined battery 2:lithium battery 3:SEALED_LEAD battery 4:AGM battery 5:GEL battery 6:FLOODED battery | the default value is 4；effective range：0,6
10111 | WR | Battery AH | 1AH | effective range：(0-900)AH the default value is 100AH
10112 | WR | Remove the accumulated data | 0：No remove the accumulated data 1：Remove the accumulated data | the default value is 0；effective range：0,1
10118 | WR | Battery equalization enable | 0:Disable 1:Enable | effective range：0,1 the default value is 0；
10119 | WR | Battery Equalization voltage | 0.1V | 48V:480-640(48.0-64.0)V the default value is 58.4V 24V:240-320(24.0-32.0)V the default value is 29.2V 12V:120-160(12.0-16.0)V the default value is 14.6V
10120 | WR | reserved | reserved
10121 | WR | Battery equalized time | 1min | 5-900(5-900)min the default value is 150min
10122 | WR | Battery Equalized timeout | 1min | 5-900(5-900)min the default value is 150min
10123 | WR | Equalization interval | 1day | 0-90(0-90)day the default value is 30 days
10124 | WR | Equalization actived immediately | 0:No effect 1:Action | the default value is 0; effective range:0,1
Register Address（decimalism） | Register Type | Register Name | Physical Unit | Effective Range | note
PV Charger Display Message
15201 | RO | Charger workstate | 0：Initialization mode 1：Selftest Mode 2: Work Mode 3：Stop Mode
15202 | RO | Mppt state | 0：Stop 1：MPPT 2: Current limiting
15203 | RO | charging state | 0:Stop 1:Absorb charge 2: Float charge 3:EQ charge
15204 | RO | reserved
15205 | RO | PV voltage | 0.1V | (0.0-150.0)V
15206 | RO | Battery voltage | 0.1V | (0.0-80.0)V
15207 | RO | Charger current | 0.1A | (0.0-90.0)A
15208 | RO | Charger power | 1W | (0-5000)W
15209 | RO | Radiator temperature | 1℃ | (-40-150)℃
15210 | RO | External temperature | 1℃ | (-40-150)℃
15211 | RO | Battery Relay |  | 0: Disconnect 1:Connect
15212 | RO | PV Relay |  | 0: Disconnect 1:Connect
15213 | RO | Error message | Refer to frame Charger Error message 1
15214 | RO | Warning message | Refer to frame Charger Warning message 1
15215 | RO | BattVol Grade | 1V
15216 | RO | Rated Current | 0.1A
15217 | RO | Accumulated PV power high | 1000KWH
15218 | RO | Accumulated PV power low | 0.1KWH
15219 | RO | Accumulated day | 1day
15220 | RO | Accumulated hour | 1hour
15221 | RO | Accumulated minute | 1minute

## PV Charger Alarm
Charger error message 1 |  |  | Charger Warning message 1
Bit | meaning | description | Charger Warning message 1 | meaning | description
0 | Hardware protection | 0：normal 1：fault | 0 | Fan Error | 0：normal 1：fault
1 | Over current | 0：normal 1：fault | 1 | reserved | 0：normal 1：fault
2 | Current sensor error | 0：normal 1：fault | 2 | reserved | 0：normal 1：fault
3 | Over temperature | 0：normal 1：fault | 3 | reserved | 0：normal 1：fault
4 | PV voltage is too high | 0：normal 1：fault | 4 | reserved | 0：normal 1：fault
5 | PV voltage is too low | 0：normal 1：fault | 5 | reserved | 0：normal 1：fault
6 | Battery voltage is too high | 0：normal 1：fault | 6 | reserved | 0：normal 1：fault
7 | Battery voltage is too Low | 0：normal 1：fault | 7 | reserved | 0：normal 1：fault
8 | Current is uncontrollable | 0：normal 1：fault | 8 | reserved | 0：normal 1：fault
9 | Parameter error | 0：normal 1：fault | 9 | reserved | 0：normal 1：fault
10 | reserved | 0：normal 1：fault | 10 | reserved | 0：normal 1：fault
11 | reserved | 0：normal 1：fault | 11 | reserved | 0：normal 1：fault
12 | reserved | 0：normal 1：fault | 12 | reserved | 0：normal 1：fault
13 | reserved | 0：normal 1：fault | 13 | reserved | 0：normal 1：fault
14 | reserved | 0：normal 1：fault | 14 | reserved | 0：normal 1：fault
15 | reserved | 0：normal 1：fault | 15 | reserved | 0：normal 1：fault